SETUP PROCEDURES FOR THE ELREHA DEFROST TIMER

- Change the defrost timer’s parameters so they match the values on the next 2 pages.

- When changing a parameter on the defrost timer, first the P30 parameter will have to be 	adjusted.  Once the P30 parameter is adjusted to 88, the rest of the parameters are 	unlocked to be changed.  To modify the P30 parameter, follow the procedures below.

- Press the P key once to access the parameters of the defrost timer.  The display will read P03.

- To bring up the P30 parameter, press either the up or down arrow key until the display reads P30.

- Press the P key again.

- Use the up arrow key to adjust the parameter’s value to 88.

- Press the P again to select the next parameter to edit.

1/        2/          3/

P

TAR        ELREHA

3.	When the defrost timer is in the normal operation, the LEDS for output 1 and output 3 will 	be lit on the display.  This means there is 120 volt output at terminal positions 1 and 5 	on 	the back of the timer.  Terminal position 1 has an output when LED 1 is lit and 	terminal position 5 has an output when LED 3 is lit.  Terminal position 1 is used to power a 	cooling relay, or to power the cooling solenoid.  Terminal position 5 will power the fans or a 	fan relay.

4.	When the timer is in the defrost mode, LED 2 will be lit and terminal position 4 will have a 	120 volt output that is used to power the hot gas solenoid.  The other two outputs are off.

5	After the timer terminates defrost, outputs 1 and 3 each have an independent time delay 	before the re-energize.

SETUP PROCEDURES FOR THE ELREHA DEFROST TIMER: (Cont’)

PARAMETER	DESCRIPTION	SET TO

ACTUAL TEMP.	DISPLAY

P01			CONTROL		VALUE

ACTUAL TEMP.	DISPLAY

P02			EVAPORATOR	VALUE

CONTROL

P03			SETPOINT		-49ºC

P04			HYSTERESIS	N/A

HIGH LIMIT

P05			SETPOINT		50ºC

LOW LIMIT

P06			SETPOINT		-50ºC

SWITCHING

P07			MODE RELAY 1	1

P08			DISPLAY MODE	1

CORRECTION

P09			CONTROL SNR	N/A

CORRECTION

P10			EVAP. SNR		N/A

DEFRST. TERM.

P11			TEMP.		4ºC

DEFROST

P12			METHOD		1

DEFROST

P13			FREQUENCY	4

DEFROST

P14			SAFETY		30

DEFRST. DELAY

P15			START		30

SETUP PROCEDURES FOR THE ELREHA DEFROST TIMER: (Cont’)

PARAMETER	DESCRIPTION	SET TO

RELAY 1 DELAY

P16			AFTER DEFRST.	0

FAN STOP/GO

P17			TEMPERATURE	50ºC

P18			FAN MODE		2

FAN DELAY

P19			AFTER DEFRST.	2

HIGH LIMIT

P20			ALARM		N/A

LOW LIMIT

P21			ALARM		N/A

P22			ALARM DELAY	N/A

ALARM/FAN

P23			MODE		0

HRS. TIL NEXT	DISPLAY

P24			DEFROST		VALUE

MIN. TIL		DISPLAY

P25			DEFRST. TERM.	VALUE

MIN. TIL		DISPLAY

P26			RESTART REF.	VALUE

MIN. TO GO FOR	DISPLAY

P27			FAN TO START	VALUE

MIN. TO GO FOR	DISPLAY

P28			ALARM START	VALUE

MANUAL		UP-STRT.

P29			DEFROST		DOWN-

END

ACCESS CODE	CODE IS

P30						ON PG. 1